## modbus registers
1. Instantaneous parameters
# | Modbus | [5 empty] | Remark | Remark1 | Remark2
| Modbus register | R/W | Rsgister length | Dada description | unit | content
1 | 0400 | R | 2 | INT32(3+3) | V | A phase and N-phase voltage |  | voltage
2 | 0402 |  |  |  |  | B phase and N-phase voltage
3 | 0404 |  |  |  |  | C phase and N-phase voltage
4 | 0406 |  |  |  |  | A Phase and B Phase line voltage
5 | 0408 |  |  |  |  | B Phase and C Phase line voltage
6 | 040A |  |  |  |  | C Phase and A Phase Line Voltage
7 | 040C |  |  |  |  | L-N voltage average Value |  |  | [(V A phase-N)+(V B phase-N)+(V C phase-N)]/3
8 | 040E |  |  |  |  | L-L voltage average Value |  |  | [(V L1-L2)+(V L2-L3)+(V L3-L1)]/3
9 | 0410 | R | 2 | INT32(2+3) | A | Current of A-phase |  | current
10 | 0412 |  |  |  |  | Current of B-phase
11 | 0414 |  |  |  |  | Current of C-phase
12 | 0416 |  |  |  |  | Current of N
13 | 0418 |  |  |  |  | Three-phase Vector Sum Current
14 | 041A | R | 2 | INT32(5+0) | W | A phase active power |  | active power
15 | 041C |  |  |  |  | B-phase active power
16 | 041E |  |  |  |  | C-phase active power
17 | 0420 |  |  |  |  | Combined active power
18 | 0422 | R | 2 | INT32(5+0) | VA | A phase apparent power |  | transparent power
19 | 0424 |  |  |  |  | B phase apparent power
20 | 0426 |  |  |  |  | C phase apparent power
21 | 0428 |  |  |  |  | Combined Apparent Power
22 | 042A | R | 2 | INT32(5+0) | var | A Phase reactive power |  | reactive pwoer
23 | 042C |  |  |  |  | B phase reactive power
24 | 042E |  |  |  |  | C phase reactive power
25 | 0430 |  |  |  |  | Combined reactive power
26 | 0432 | R | 1 | INT16(2+1) | Hz | A phase frequency |  | frequency
27 | 0433 |  |  |  |  | B phase frequency
28 | 0434 |  |  |  |  | C phase frequency
29 | 0435 |  |  |  |  | Combined frequency
30 | 0436 | R | 1 | INT16(1+3) | / | A phase power factor |  | power factor
31 | 0437 |  |  |  |  | B Phase power factor
32 | 0438 |  |  |  |  | C Phase power factor
33 | 0439 |  |  |  |  | Combined power factor
34 | 043A | R | 2 | INT32(6+1) | W | A phase forward active demand |  | active demand
35 | 043C |  |  |  |  | B phase forward active demand
36 | 043E |  |  |  |  | C phase forward active demand
37 | 0440 |  |  |  |  | Combined Forward Active demand
38 | 0442 |  |  |  |  | A phase reverse active demand
39 | 0444 |  |  |  |  | B phase reverse active demand
40 | 0446 |  |  |  |  | C phase reverse active demand
41 | 0448 |  |  |  |  | Combined Reverse Active Demand
42 | 044A |  |  |  |  | A phase total active power
43 | 044C |  |  |  |  | B Phase total active power
44 | 044E |  |  |  |  | C Phase total active power
45 | 0450 |  |  |  |  | Combined Active Demand
46 | 0452 | R | 2 | INT32(6+1) | var | A phase forward reactive demand |  | reactive demand
47 | 0454 |  |  |  |  | B phase forward reactive demand
48 | 0456 |  |  |  |  | C phase forward reactive demand
49 | 0458 |  |  |  |  | Combined forward reactive demand
50 | 045A |  |  |  |  | A phase reverse reactive demand
51 | 045C |  |  |  |  | B phase Reverse reactive demand
52 | 045E |  |  |  |  | C phase reverse reactive demand
53 | 0460 |  |  |  |  | Combined reverse reactive demand
54 | 0462 |  |  |  |  | A phase total reactive demand
55 | 0464 |  |  |  |  | B phase total reactive demand
56 | 0466 |  |  |  |  | C phase total reactive demand
57 | 0468 |  |  |  |  | Combined total reactive demand
58 | 046A | R | 2 | INT32(6+1) | W | A phase forward active maximum demand |  | active maximum demand
59 | 046C |  |  |  |  | B phase forward active maximum demand
60 | 046E |  |  |  |  | C phase forward active maximum demand
61 | 0470 |  |  |  |  | Combined forward active maximum demand
62 | 0472 |  |  |  |  | A phase reverse active maximum demand
63 | 0474 |  |  |  |  | B phase reverse active maximum demand
64 | 0476 |  |  |  |  | C phase reverse active maximum demand
65 | 0478 |  |  |  |  | Combined reverse active maximum demand
66 | 047A |  |  |  |  | A phase total active maximum demand
67 | 047C |  |  |  |  | B phase total active maximum demand
68 | 047E |  |  |  |  | C phase total active maximum demand
69 | 0480 |  |  |  |  | Combined total active maximum demand
70 | 0482 | R | 2 | INT32(6+1) | var | A phase forward reactive maximum demand |  | reactive maximum demand
71 | 0484 |  |  |  |  | B phase forward reactive power maximum demand
72 | 0486 |  |  |  |  | C phase forward reactive maximum demand
73 | 0488 |  |  |  |  | Combined forward reactive maximum demand
74 | 048A |  |  |  |  | A phase reverse reactive maximum demand
75 | 048C |  |  |  |  | B phase reverse reactive maximum demand
76 | 048E |  |  |  |  | C phase reverse reactive maximum demand
77 | 0490 |  |  |  |  | Combined reverse reactive maximum demand
78 | 0492 |  |  |  |  | A phase total reactive maximum demand
79 | 0494 |  |  |  |  | B phase total reactive maximum demand
80 | 0496 |  |  |  |  | C phase total reactive maximum demand
81 | 0498 |  |  |  |  | Combined total reactive maximum demand
2. Energy parameters
# | Modbus |  |  |  |  | Content | Remark | Remark1 | Remark2
| Modbus register | R/W | Rsgister length | Dada description | unit
1 | 010E | R | 2 | INT32(6+2) | kWh | Forward total active energy |  | combined energy
2 | 0110 | R | 2 | INT32(6+2) |  | T1 total forward active energy
3 | 0112 | R | 2 | INT32(6+2) |  | T2 total forward active energy
4 | 0114 | R | 2 | INT32(6+2) |  | T3 total forward active energy
5 | 0116 | R | 2 | INT32(6+2) |  | T4 total forward active energy
6 | 0118 | R | 2 | INT32(6+2) |  | Total reverse active energy
7 | 011A | R | 2 | INT32(6+2) |  | T1 total reverse active energy
8 | 011C | R | 2 | INT32(6+2) |  | T2 total reverse active energy
9 | 011E | R | 2 | INT32(6+2) |  | T3 total reverse active energy
10 | 0120 | R | 2 | INT32(6+2) |  | T4 total reverse active energy
11 | 0122 | R | 2 | INT32(6+2) |  | Active total energy
12 | 0124 | R | 2 | INT32(6+2) |  | T1 total active energy
13 | 0126 | R | 2 | INT32(6+2) |  | T2 total active energy
14 | 0128 | R | 2 | INT32(6+2) |  | T3 total active energy
15 | 012A | R | 2 | INT32(6+2) |  | T4 total active energy
16 | 012C | R | 2 | INT32(6+2) | kvarh | Total forward reactive energy
17 | 012E | R | 2 | INT32(6+2) |  | T1 total forward reactive energy
18 | 0130 | R | 2 | INT32(6+2) |  | T2 total forward reactive energy
19 | 0132 | R | 2 | INT32(6+2) |  | T3 total forward reactive energy
20 | 0134 | R | 2 | INT32(6+2) |  | T4 total forward reactive energy
21 | 0136 | R | 2 | INT32(6+2) |  | Total reverse reactive energy
22 | 0138 | R | 2 | INT32(6+2) |  | T1 total reverse reactive energy
23 | 013A | R | 2 | INT32(6+2) |  | T2 total reverse reactive energy
24 | 013C | R | 2 | INT32(6+2) |  | T3 total reverse reactive energy
25 | 013E | R | 2 | INT32(6+2) |  | T4 total reverse reactive energy
26 | 0140 | R | 2 | INT32(6+2) |  | Total reactive energy
27 | 0142 | R | 2 | INT32(6+2) |  | T1 total reactive energy
28 | 0144 | R | 2 | INT32(6+2) |  | T2 total reactive energy
29 | 0146 | R | 2 | INT32(6+2) |  | T3 total reactive energy
30 | 0148 | R | 2 | INT32(6+2) |  | T4 total reactive energy
31 | 014A | R | 2 | INT32(6+2) |  | The first quadrant Total reactive energy
32 | 014C | R | 2 | INT32(6+2) |  | T1 first quadrant total reactive energy
33 | 014E | R | 2 | INT32(6+2) |  | T2 first quadrant total reactive energy
34 | 0150 | R | 2 | INT32(6+2) |  | T3 first quadrant total reactive energy
35 | 0152 | R | 2 | INT32(6+2) |  | T4 first quadrant total reactive energy
36 | 0154 | R | 2 | INT32(6+2) |  | The second quadrant total reactive energy
37 | 0156 | R | 2 | INT32(6+2) |  | T1 second quadrant total reactive energy
38 | 0158 | R | 2 | INT32(6+2) |  | T2 second quadrant total reactive energy
39 | 015A | R | 2 | INT32(6+2) |  | T3 second quadrant total reactive energy
40 | 015C | R | 2 | INT32(6+2) |  | T4 second quadrant total reactive energy
41 | 015E | R | 2 | INT32(6+2) |  | The third quadrant total reactive energy
42 | 0160 | R | 2 | INT32(6+2) |  | T1 third quadrant total reactive energy
43 | 0162 | R | 2 | INT32(6+2) |  | T2 third quadrant total reactive energy
44 | 0164 | R | 2 | INT32(6+2) |  | T3 third quadrant total reactive energy
45 | 0166 | R | 2 | INT32(6+2) |  | T4 third quadrant total reactive energy
46 | 0168 | R | 2 | INT32(6+2) |  | The fourth quadrant total reactive energy
47 | 016A | R | 2 | INT32(6+2) |  | T1 fourth quadrant total reactive energy
48 | 016C | R | 2 | INT32(6+2) |  | T2 fourth quadrant total reactive energy
49 | 016E | R | 2 | INT32(6+2) |  | T3 fourth quadrant total reactive energy
50 | 0170 | R | 2 | INT32(6+2) |  | T4 fourth quadrant total reactive energy
51 | 0500 | R | 2 | INT32(6+2) | kWh | A phase total active energy |  | A phase energy
52 | 0502 |  |  |  |  | A phase T1 total active energy
53 | 0504 |  |  |  |  | A phase T2 total active energy
54 | 0506 |  |  |  |  | A phase T3 total active energy
55 | 0508 |  |  |  |  | A phase T4 total active energy
56 | 050A |  |  |  |  | A phase forward active energy
57 | 050C |  |  |  |  | A phase T1 forward active energy
58 | 050E |  |  |  |  | A phase T2 forward active energy
59 | 0510 |  |  |  |  | A phase T3 forward active energy
60 | 0512 |  |  |  |  | A phase T4 forward active energy
61 | 0514 |  |  |  |  | A phase reverse active energy
62 | 0516 |  |  |  |  | A phase T1 reverse active energy
63 | 0518 |  |  |  |  | A phase T2 reverse active energy
64 | 051A |  |  |  |  | A phase T3 reverse active energy
65 | 051C |  |  |  |  | A phase T4 reverse active energy
66 | 051E | R | 2 | INT32(6+2) | kvarh | A phase total reactive energy
67 | 0520 |  |  |  |  | A phase T1 total reactive energy
68 | 0522 |  |  |  |  | A phase T2 total reactive energy
69 | 0524 |  |  |  |  | A phase T3 total reactive energy
70 | 0526 |  |  |  |  | A phase T4 total reactive energy
71 | 0528 |  |  |  |  | A phase forward reactive energy
72 | 052A |  |  |  |  | A phase T1 forward reactive energy
73 | 052C |  |  |  |  | A phase T2 forward reactive energy
74 | 052E |  |  |  |  | A phase T3 forward reactive energy
75 | 0530 |  |  |  |  | A phase T4 forward reactive energy
76 | 0532 |  |  |  |  | A phase reverse reactive energy
77 | 0534 |  |  |  |  | A phase T1 reverse reactive energy
78 | 0536 |  |  |  |  | A phase T2 reverse reactive energy
79 | 0538 |  |  |  |  | A phase T3 reverse reactive energy
80 | 053A |  |  |  |  | A phase T4 reverse reactive energy
81 | 053C |  |  |  |  | A phase first quadrant total reactive energy
82 | 053E |  |  |  |  | A phase T1 first quadrant total reactive energy
83 | 0540 |  |  |  |  | A phase T2 first quadrant total reactive energy
84 | 0542 |  |  |  |  | A phase T3 first quadrant total reactive energy
85 | 0544 |  |  |  |  | A phase T4 first quadrant total reactive energy
86 | 0546 |  |  |  |  | A phase sencond quadrant total reactive energy
87 | 0548 |  |  |  |  | A phase T1 second quadrant total reactive energy
88 | 054A |  |  |  |  | A phase T2 second quadrant total reactive energy
89 | 054C |  |  |  |  | A phase T3 second quadrant total reactive energy
90 | 054E |  |  |  |  | A phase T4 second quadrant total reactive energy
91 | 0550 |  |  |  |  | A phase third quadrant total reactive energy
92 | 0552 |  |  |  |  | A phase T1 third quadrant total reactive energy
93 | 0554 |  |  |  |  | A phase T2 third quadrant total reactive energy
94 | 0556 |  |  |  |  | A phase T3 third quadrant total reactive energy
95 | 0558 |  |  |  |  | A phase T4 third quadrant total reactive energy
96 | 055A |  |  |  |  | A phase fourth quadrant total reactive energy
97 | 055C |  |  |  |  | A phase T1 fourth quadrant total reactive energy
98 | 055E |  |  |  |  | A phase T2 fourth quadrant total reactive energy
99 | 0560 |  |  |  |  | A phase T3 fourth quadrant total reactive energy
100 | 0562 |  |  |  |  | A phase T4 fourth quadrant total reactive energy
101 | 0564 | R | 2 | INT32(6+2) | kWh | B phase total active energy |  | B Phase energy
102 | 0566 |  |  |  |  | B phase T1 total active energy
103 | 0568 |  |  |  |  | B phase T2 total active energy
104 | 056A |  |  |  |  | B phase T3 total active energy
105 | 056C |  |  |  |  | B phase T4 total active energy
106 | 056E |  |  |  |  | B phase forward active energy
107 | 0570 |  |  |  |  | B phase T1 forward active energy
108 | 0572 |  |  |  |  | B phase T2 forward active energy
109 | 0574 |  |  |  |  | B phase T3 forward active energy
110 | 0576 |  |  |  |  | B phase T4 forward active energy
111 | 0578 |  |  |  |  | B phase reverse active energy
112 | 057A |  |  |  |  | B phase T1 reverse active energy
113 | 057C |  |  |  |  | B phase T2 reverse active energy
114 | 057E |  |  |  |  | B phase T3 reverse active energy
115 | 0580 |  |  |  |  | B phase T4 reverse active energy
116 | 0582 | R | 2 | INT32(6+2) | kvarh | B phase total reactive energy
117 | 0584 |  |  |  |  | B phase T1 Total reactive energy
118 | 0586 |  |  |  |  | B phase T2 Total reactive energy
119 | 0588 |  |  |  |  | B phase T3 total reactive energy
120 | 058A |  |  |  |  | B phaseT4 Total reactive energy
121 | 058C |  |  |  |  | B phase forward reactive energy
122 | 058E |  |  |  |  | B phase T1 forward reactive energy
123 | 0590 |  |  |  |  | B phase T2 forward reactive energy
124 | 0592 |  |  |  |  | B phase T3 forward reactive energy
125 | 0594 |  |  |  |  | B phase T4 forward reactive energy
126 | 0596 |  |  |  |  | B phase Reverse reactive energy
127 | 0598 |  |  |  |  | B phase T1 reverse reactive energy
128 | 059A |  |  |  |  | B phase T2 reverse reactive energy
129 | 059C |  |  |  |  | B phase T3 reverse reactive energy
130 | 059E |  |  |  |  | B phase T4 reverse reactive energy
131 | 05A0 |  |  |  |  | B phase first quadrant total reactive energy
132 | 05A2 |  |  |  |  | B phase T1 first quadrant total reactive energy
133 | 05A4 |  |  |  |  | B phase T2 first quadrant total reactive energy
134 | 05A6 |  |  |  |  | B phase T3 first quadrant total reactive energy
135 | 05A8 |  |  |  |  | B phase T4 first quadrant total reactive energy
136 | 05AA |  |  |  |  | B phase second quadrant total reactive energy
137 | 05AC |  |  |  |  | B phase T1 second quadrant total reactive energy
138 | 05AE |  |  |  |  | B phase T2 second quadrant total reactive energy
139 | 05B0 |  |  |  |  | B phase T3 second quadrant total reactive energy
140 | 05B2 |  |  |  |  | B phase T4 second quadrant total reactive energy
141 | 05B4 |  |  |  |  | B phase third quadrant total reactive energy
142 | 05B6 |  |  |  |  | B phase T1 third quadrant total reactive energy
143 | 05B8 |  |  |  |  | B phase T2 third quadrant total reactive energy
144 | 05BA |  |  |  |  | B phase T3 third quadrant total reactive energy
145 | 05BC |  |  |  |  | B phase T4 third quadrant total reactive energy
146 | 05BE |  |  |  |  | B phase fourth quadrant total reactive energy
147 | 05C0 |  |  |  |  | B phase T1 fourth quadrant total reactive energy
148 | 05C2 |  |  |  |  | B phase T2 fourth quadrant total reactive energy
149 | 05C4 |  |  |  |  | B phase T3 fourth quadrant total reactive energy
150 | 05C6 |  |  |  |  | B phase T4 fourth quadrant total reactive energy
151 | 05C8 | R | 2 | INT32(6+2) | kWh | Phase C total active energy |  | C phase energy
152 | 05CA |  |  |  |  | C-phase T1 total active energy
153 | 05CC |  |  |  |  | C-phase T2 total active energy
154 | 05CE |  |  |  |  | C-phase T3 total active energy
155 | 05D0 |  |  |  |  | C-phase T4 total active energy
156 | 05D2 |  |  |  |  | C-phase forward active energy
157 | 05D4 |  |  |  |  | C-phase T1 forward active energy
158 | 05D6 |  |  |  |  | C-phase T2 forward active energy
159 | 05D8 |  |  |  |  | C-phase T3 forward active energy
160 | 05DA |  |  |  |  | C-phase T4 forward active energy
161 | 05DC |  |  |  |  | C phase reverse active energy
162 | 05DE |  |  |  |  | C-phase T1 reverse active energy
163 | 05E0 |  |  |  |  | C-phase T2 reverse active energy
164 | 05E2 |  |  |  |  | C-phase T3 reverse active energy
165 | 05E4 |  |  |  |  | C-phase T4 reverse active energy
166 | 05E6 | R | 2 | INT32(6+2) | kvarh | Total reactive energy of phase C
167 | 05E8 |  |  |  |  | C-phase T1 total reactive energy
168 | 05EA |  |  |  |  | C-phase T2 total reactive energy
169 | 05EC |  |  |  |  | C-phase T3 total reactive energy
170 | 05EE |  |  |  |  | C-phase T4 total reactive energy
171 | 05F0 |  |  |  |  | C-phase forward reactive energy
172 | 05F2 |  |  |  |  | C-phase T1 forward reactive energy
173 | 05F4 |  |  |  |  | C-phase T2 forward reactive energy
174 | 05F6 |  |  |  |  | C-phase T3 forward reactive energy
175 | 05F8 |  |  |  |  | C-phase T4 forward reactive energy
176 | 05FA |  |  |  |  | C phase reverse reactive energy
177 | 05FC |  |  |  |  | C-phase T1 reverse reactive energy
178 | 05FE |  |  |  |  | C-phase T2 reverse reactive energy
179 | 0600 |  |  |  |  | C-phase T3 reverse reactive energy
180 | 0602 |  |  |  |  | C-phase T4 reverse reactive energy
181 | 0604 |  |  |  |  | C phase first quadrant total reactive energy
182 | 0606 |  |  |  |  | C phase T1 first quadrant total reactive energy
183 | 0608 |  |  |  |  | C phase T2 first quadrant total reactive energy
184 | 060A |  |  |  |  | C phase T3 first quadrant total reactive energy
185 | 060C |  |  |  |  | C phase T4 first quadrant total reactive energy
186 | 060E |  |  |  |  | C phase second quadrant total reactive energy
187 | 0610 |  |  |  |  | C phase T1 second quadrant total reactive energy
188 | 0612 |  |  |  |  | C phase T2 second quadrant total reactive energy
189 | 0614 |  |  |  |  | C phase T3 second quadrant total reactive energy
190 | 0616 |  |  |  |  | C phase T4 second quadrant total reactive energy
191 | 0618 |  |  |  |  | C phase third quadrant total reactive energy
192 | 061A |  |  |  |  | C phase T1 third quadrant total reactive energy
193 | 061C |  |  |  |  | C phase T2 third quadrant total reactive energy
194 | 061E |  |  |  |  | C phase T3 third quadrant total reactive energy
195 | 0620 |  |  |  |  | C phase T4 third quadrant total reactive energy
196 | 0622 |  |  |  |  | C phase fourth quadrant total reactive energy
197 | 0624 |  |  |  |  | C phase T1 fourth quadrant total reactive energy
198 | 0626 |  |  |  |  | C phase T2 fourth quadrant total reactive energy
199 | 0628 |  |  |  |  | C phase T3 fourth quadrant total reactive energy
200 | 062A |  |  |  |  | C phase T4 fourth quadrant total reactive energy
201 | 062C | R | 2 | INT32(6+2) | kWh | Active resettable energy |  | resettable energy
202 | 062E |  |  |  |  | foward active resettable energy
203 | 0630 |  |  |  |  | Reverse active resettable energy
204 | 0632 |  |  |  |  | A-phase active resettable energy
205 | 0634 |  |  |  |  | A-phase foward active resettable energy
206 | 0636 |  |  |  |  | A phase reverse active resettable energy
207 | 0638 |  |  |  |  | B-phase active resettable energy
208 | 063A |  |  |  |  | B-phase forward active resettable energy
209 | 063C |  |  |  |  | B phase reverse active resettable energy
210 | 063E |  |  |  |  | C-phase active energy resettable energy
211 | 0640 |  |  |  |  | C-phase foward active resettable energy
212 | 0642 |  |  |  |  | Phase C reverse active resettable energy
213 | 0644 | R | 2 | INT32(6+2) | kvarh | Reactive resettable energy
214 | 0646 |  |  |  |  | foward reactive resettable energy
215 | 0648 |  |  |  |  | Reverse reactive resettable energy
216 | 064A |  |  |  |  | A-phase reactive resettable energy
217 | 064C |  |  |  |  | A-phase forward reactive resettable energy
218 | 064E |  |  |  |  | A phase reverse reactive resettable energy
219 | 0650 |  |  |  |  | B-phase reactive resettable energy
220 | 0652 |  |  |  |  | B-phase forward reactive resettable energy
221 | 0654 |  |  |  |  | B phase reverse reactive resettable energy
222 | 0656 |  |  |  |  | Phase C reactive energy resettable energy
223 | 0658 |  |  |  |  | C-phase forward reactive resettable energy
224 | 065A |  |  |  |  | C phase reverse reactive resettable energy
3 Meter parameters
Modbus
# | Modbus register | R/W | Rsgister length | Dada description | unit | content |  | Remark1
1 | 1000 | 6 | R.W | 12-bit serial number,the same as DLT645 address, need to use 10h together,hexadecimal, 012345678910H serial number is 012345678910 |  | serial number
2 | 1003 | 1 | R.W | 1-247 |  | Modbus ID/Mbus ID
3 | 1004 | 1 | R | 101 |  | software version number
4 | 1005 | 1 | R | 101 |  | Hardware version number
5 | 1006 | 1 | R | XXXX |  | Firmware Checksum
6 | 1007 | 4 | R.W | 00 year, month, day, week, hour, minute, second, need to use 10 control code to write at one time |  | time
7
8 | 100B | 1 | R.W | 0-99 seconds (0 disables scroll display) |  | Turn time
9 | 100C | 1 | R.W | 6=9600 7=19200 8=38400 9=115200 |  | 485 baud rate
10 | 100D | 1 | R.W | 0=none 1=odd 2=even |  | Parity
11 | 100E | 1 | R.W | 1=1 bit 2=2 bit |  | 485 stop bit
12 | 100F | 1 | R.W | 1-Total=Forward 2-Total=Reverse 3-Total=Forward+Reverse 4-Total=Forward-Reverse |  | combined code
13 | 1010 | 1 |  | 0=Interval 1=Slip |  | demand mode
14 | 1011 | 1 | R.W | The unit minute, can be set from 1-30, the default is 15 minutes |  | demand cycle
15 | 1016 | 1 | R.W | 0000-9999 can be set |  | LCD button display password setting
16 | 1017 | 1 | R.W | 800, 1000, 1600, etc. above 100,divisible by 96000 |  | SO output
17 | 1018 | 2 | R.W | The running time of the electric meter (starting to calculate when it is greater than the setted current), write 0 to clear to 0, need to use the 10 control code to write at one time |  | Meter running time
18 | 101A | 2 | R.W | The unit is mA (the default is the startup current, the maximum current is 1.2 times), and the 10 control code needs to be written at one time. |  | Set the timing current value
19 | 101D | 1 | R | Terminal signal input status |  | 0 or 1
20 | 1020 | 5 | R.W | Bit-wise mark, BIT0 represents total active energy, BIT1 represents positive active energy, see the three-phase display description scrolling display page for details. Total energy & instantaneous parameters |  | Automatic scroll display content (three-phase)
21 | 2001 | 1 | W | bit0-L1 resettable total forward active energy bit1-L2 resettable total forward active energy bit2-L3 resettable total forward active energy bit3-L1 resettable total reverse active energy bit4-L2 resettable total reverse active energyr bit5-L3 resettable total reverse active energy bit6-L1 resettable total forward reactive energy bit7-L2 resettable total forward reactive energy bit8-L3 resettable total forward reactive energy bit9-L1 resettable total reverse reactive energy bit10-L2 resettable total reverse reactive energy bit11-L3 resettable total reverse reactive energy bit12-Resettable total active energy bit13-Resettable total reactive energy |  | Clear Energy
22 | 2002 | 1 | W | FFA5 clear all A5XX clear part, see the description below bit0= forward active maximum demand bit1=reverse active maximum demand bit2=forward reactive maximum demand bit3=forward reactive maximum demand bit4=active maximum demand bit5=reactive maximum demand bit6-bit7 00 phase combination 01A phase 10B phase 11C phase |  | Clear maximum demand
3. Tariff Parameters
# | Modbus
| Modbus register | R/W | Rsgister length | Dada description | unit | Content
1 | 1700 | R.W | 12 | hhmmNN*8 Need to use 10h to write together |  | Timetable 1
2 | 170C | R.W | 12 |  |  | Timetable 2
3 | 1718 | R.W | 12 |  |  | Timetable 3
4 | 1724 | R.W | 12 |  |  | Timetable 4
5 | 1730 | R.W | 12 |  |  | Timetable 5
6 | 173C | R.W | 12 |  |  | Timetable 6
7 | 1748 | R.W | 12 |  |  | Timetable 7
8 | 1754 | R.W | 12 |  |  | Timetable 8
9 | 1760 | R.W | 12 | MMDDNN*8 |  | time zone table
10 | 176C | R.W | 21 | MMDDNN*14 |  | holiday table

## SO output description
Combination code (Measurement mode) | SO Output number | SO Output mode | SO output descrption | SO Output LED | Total energy description
Forward only | SO-1 | Active forward | Only output active forward pulse | Only output positive active pulse | Total energy = Forward energy, no sign for energy in communication and display
| SO-2 | Reactive forward | Only output reactive forward pulse
Reverse Only | SO-1 | Active reverse | Only Output active reverse pulse | Output only reverse active pulses | Total energy = reverse energy, with sign for energy in communication and display
| SO-2 | Reactive reverse | Only output reactive reverse pulse
Absolute (Forward+Reverse) | SO-1 | Absolute active （Default） | Output absolute value (forward + reverse) active pulse | Output absolute value (Forward + reverse) active pulse | Total energy =Forward+ reverse energy, without sign for energy in communication and display
|  | Active forward | output active forward pulse
|  | Reactive forward | Only output reactive forward pulse
| SO-2 | Absolute Reactive （Default） | Output absolute value (forward + reverse) reactive pulse
|  | Active reverse | Only Output active reverse pulse
|  | Reactive reverse | Only output reactive reverse pulse
Algebraic Sum (Forward-Inverse) | SO-1 | Absolute active （Default） | Output absolute value (forward + reverse) active pulse | Output absolute value (Forward + reverse) active pulse | Total energy =Forward- reverse energy, with sign for energy in communication and display if reverse>Forward
|  | Active forward | Only output active forward pulse
|  | Reactive forward | Only output reactive forward pulse
| SO-2 | Absolute Reactive （Default） | Output absolute value (forward + reverse) reactive pulse
|  | Active reverse | Only Output active reverse pulse
|  | Reactive reverse | Only output reactive reverse pulse
Combination code (Measurement mode) | SO Output number | SO Output mode | SO output descrption | SO Output LED | Total energy description
Forward only | SO | positive active | Only output positive active pulse | Only output positive active pulse | Total energy = Forward energy, no sign for energy in communication and display
Reverse Only | SO | reverse active | Output only reverse active pulses | Output only reverse active pulses | Total energy = reverse energy, with sign for energy in communication and display
Absolute (Forward+Reverse) | SO | Active | Output absolute value (positive + negative) active pulse | Output absolute value (positive + negative) active pulse | Total energy =Forward+ reverse energy, without sign for energy in communication and display
Algebraic Sum (Forward-Inverse) | SO | Active | Output absolute value (positive + negative) active pulse | Output absolute value (positive + negative) active pulse | Total energy =Forward- reverse energy, with sign for energy in communication and display if reverse>Forward

## LCD display
Wheel display page |  |  |  | Phase A battery |  |  | B phase power |  |  | Phase C power |  |  | information page
page number | Display content | Display description | Long press the left button for more than 3 seconds -> | page number | Display content | Long press the left button for more than 3 seconds -> | page number | Display conent | -> Long press the left button for more than 3 seconds → | page number | Display content | Long press the left button for more than 3 seconds -> | page number | Display content | Display description
1 | Total active energy | Display 6+2(7+1)kwh |  | 1 | Total active energy |  | 1 | Total active energy |  | 1 | Total active energy |  | 1 | Serial number | 12 digit，000000000000
2 | Forward active energy | Display 6+2(7+1)kwh |  | 2 | Forward active energy |  | 2 | Forward active energy |  | 2 | Forward active energy |  | 2 | Modbus ID | 1-247
3 | Reverse active energyr | With sign '-', display 5+2(6+1)(7)kwh |  | 3 | Reverse active energyr |  | 3 | Reverse active energyr |  | 3 | Reverse active energyr |  | 3 | Baud rate | 9600/19200/38400/115200
4 | T1 active energy | Display 6+2(7+1)kwh |  | 4 | T1 active energy |  | 4 | T1 active energy |  | 4 | T1 active energy |  | 4 | Parity | Odd/Even/None
5 | T1 forward active energy | Display 6+2(7+1)kwh |  | 5 | T1 forward active energy |  | 5 | T1 forward active energy |  | 5 | T1 forward active energy |  | 5 | stop bit | 1/2bit
6 | T1 Reverse active energy | With sign '-', display 5+2(6+1)(7)kwh |  | 6 | T1 reverse active energy |  | 6 | T1 reverse active energy |  | 6 | T1 Reverse active energy |  | 6 | scrolling time | 5-99 seconds, 0 disables scroll displa
7 | T2 active energy | Display 6+2(7+1)kwh |  | 7 | T2 active energy |  | 7 | T2 active energy |  | 7 | T2 active energy |  | 7 | Combined code | 1=Total=Forward 2=Total=Reverse 3=Total=Forward+Reverse 4=Total=Forward-Reverse
8 | T2 forward active energy | Display 6+2(7+1)kwh |  | 8 | T2 forward active energy |  | 8 | T2 forward active energy |  | 8 | T2 forward active energy |  | 8 | Demand Type and Period | Type 0 interval 1 slip, period 1-30 minutes
9 | T2 Reverse active energ | With sign '-', display 5+2(6+1)(7)kwh |  | 9 | T2 reverse active energy |  | 9 | T2 reverse active energy |  | 9 | T2 Reverse active energy |  | 9 | SO output | 800, 1000, 1600, etc. above 100,divisible by 96000
10 | T3 active energy | Display 6+2(7+1)kwh |  | 10 | T3 active energy |  | 10 | T3 active energy |  | 10 | T3 active energy |  | 10 | Date | DDMMYY
11 | T3 forward active energy | Display 6+2(7+1)kwh |  | 11 | T3 forward active energy |  | 11 | T3 forward active energy |  | 11 | T3 forward active energy |  | 11 | Time | HHMMSS
12 | T3 Reverse active energ | With sign '-', display 5+2(6+1)(7)kwh |  | 12 | T3 reverse active energy |  | 12 | T3 reverseactive energy |  | 12 | T3 Reverse active energy |  | 12 | version number | U101
13 | T4 active energy | Display 6+2(7+1)kwh |  | 13 | T4 active energy |  | 13 | T4 active energy |  | 13 | T4 active energy |  | 13 | checksum | XXXX
14 | T4 forward active energy | Display 6+2(7+1)kwh |  | 14 | T4 forward active energy |  | 14 | T4 forward active energy |  | 14 | T4 forward active energy
15 | T4 Reverse active energ | With sign '-', display 5+2(6+1)(7)kwh |  | 15 | T4 reverse active energy |  | 15 | T4 reverse active energy |  | 15 | T4 Reverse active energy
16 | Total reactive energy | Display 6+2(7+1)kvarh |  | 16 | Total reactive energy |  | 16 | Total reactive energy |  | 16 | Total reactive energy
17 | Forward reactive energy | Display 6+2(7+1)kvarh |  | 17 | Forward reactive energy |  | 17 | Forward reactive energy |  | 17 | Forward reactive energy
18 | Reverse reactive energyr | With sign '-', display 5+2(6+1)(7)kvarh |  | 18 | Reverse reactive energyr |  | 18 | Reverse reactive energyr |  | 18 | Reverse reactive energyr
19 | first quadrant reactive energy | Display 6+2(7+1)kvarh |  | 19 | first quadrant reactive energy |  | 19 | first quadrant reactive energy |  | 19 | first quadrant reactive energy
20 | second quadrant reactive energy | Display 6+2(7+1)kvarh |  | 20 | second quadrant reactive energy |  | 20 | second quadrant reactive energy |  | 20 | second quadrant reactive energy
21 | third quadrant reactive energy | Display 6+2(7+1)kvarh |  | 21 | third quadrant reactive energy |  | 21 | third quadrant reactive energy |  | 21 | third quadrant reactive energy
22 | forth quadrant reactive energy | Display 6+2(7+1)kvarh |  | 22 | forth quadrant reactive energy |  | 22 | forth quadrant reactive energy |  | 22 | forth quadrant reactive energy
23 | T1 reactive energy | Display 6+2(7+1)kvarh |  | 23 | T1 reactive energy |  | 23 | T1 reactive energy |  | 23 | T1 reactive energy
24 | T1 forward reactive energy | Display 6+2(7+1)kvarh |  | 24 | T1 forward reactive energy |  | 24 | T1 forward reactive energy |  | 24 | T1 forward reactive energy
25 | T1 reverse reactive energy | With sign '-', display 5+2(6+1)(7)kvarh |  | 25 | T1 reverse reactive energy |  | 25 | T1 reverse reactive energy |  | 25 | T1 Reverse reactive energy
26 | T2 reactive energy | Display 6+2(7+1)kvarh |  | 26 | T2 reactive energy |  | 26 | T2 reactive energy |  | 26 | T2 reactive energy
27 | T2 forward reactive energy | Display 6+2(7+1)kvarh |  | 27 | T2 forward reactive energy |  | 27 | T2 forward reactive energy |  | 27 | T2 forward reactive energy
28 | T2 Reverse reactive energy | With sign '-', display 5+2(6+1)(7)kvarh |  | 28 | T2 reverse reactive energy |  | 28 | T2 reverse reactive energy |  | 28 | T2 Reverse reactive energy
29 | T3 reactive energy | Display 6+2(7+1)kvarh |  | 29 | T3 reactive energy |  | 29 | T3 reactive energy |  | 29 | T3 reactive energy
30 | T3 forward reactive energy | Display 6+2(7+1)kvarh |  | 30 | T3 forward reactive energy |  | 30 | T3 forward reactive energy |  | 30 | T3 forward reactive energy
31 | T3 Reverse reactive energy | With sign '-', display 5+2(6+1)(7)kvarh |  | 31 | T3 reverse reactive energy |  | 31 | T3 reverse reactive energy |  | 31 | T3 Reverse reactive energy
32 | T4 reactive energy | Display 6+2(7+1)kvarh |  | 32 | T4 reactive energy |  | 32 | T4 reactive energy |  | 32 | T4 reactive energy
33 | T4 forward reactive energy | Display 6+2(7+1)kvarh |  | 33 | T4 forward reactive energy |  | 33 | T4 forward reactive energy |  | 33 | T4 forward reactive energy
34 | T4 Reverse reactive energy | With sign '-', display 5+2(6+1)(7)kvarh |  | 34 | T4 reverse reactive energy |  | 34 | T4 reverse reactive energy |  | 34 | T4 Reverse reactive energy
35 | Active resettable energy | Display 6+2(7+1)kvarh |  | 35 | Active resettable energy |  | 35 | Active resettable energy |  | 35 | Active resettable energy
36 | foward active resettable energy | Display 6+2(7+1)kvarh |  | 36 | foward active resettable energy |  | 36 | foward active resettable energy |  | 36 | foward active resettable energy
37 | Reverse active resettable energy | With sign '-', display 5+2(6+1)(7)kvarh |  | 37 | Reverse active resettable energy |  | 37 | Reverse active resettable energy |  | 37 | Reverse active resettable energy
38 | Reactive resettable energy | Display 6+2(7+1)kvarh |  | 38 | Reactive resettable energy |  | 38 | Reactive resettable energy |  | 38 | Reactive resettable energy
39 | foward reactive resettable energy | Display 6+2(7+1)kvarh |  | 39 | foward reactive resettable energy |  | 39 | foward reactive resettable energy |  | 39 | foward reactive resettable energy
40 | Reverse reactive resettable energy | With sign '-', display 5+2(6+1)(7)kvarh |  | 40 | Reverse reactive resettable energy |  | 40 | Reverse reactive resettable energy |  | 40 | Reverse reactive resettable energy
41 | Active maximum demand | Display 6+2(7+1)kvarh |  | 41 | Active maximum demand |  | 41 | Active maximum demand |  | 41 | Active maximum demand
42 | Forward active maximum demand | Display 6+2(7+1)kvarh |  | 42 | Forward active maximum demand |  | 42 | Forward active maximum demand |  | 42 | Forward active maximum demand
43 | Reverse active maximum demand | With sign '-', display 5+2(6+1)(7)kvarh |  | 43 | Reverse active maximum demand |  | 43 | Reverse active maximum demand |  | 43 | Reverse active maximum demand
44 | Reactive maximum demand | Display 6+2(7+1)kvarh |  | 44 | Reactive maximum demand |  | 44 | Reactive maximum demand |  | 44 | Reactive maximum demand
45 | Forward reactive maximum demand | Display 6+2(7+1)kvarh |  | 45 | Forward reactive maximum demand |  | 45 | Forward reactive maximum demand |  | 45 | Forward reactive maximum demand
46 | Reverse reactive maximum demand | With sign '-', display 5+2(6+1)(7)kvarh |  | 46 | Reverse reactive maximum demand |  | 46 | Reverse reactive maximum demand |  | 46 | Reverse reactive maximum demand
47 | A phase and N-phase voltage | Display 3+2 V
48 | B phase and N-phase voltage | Display 3+2 V
49 | C phase and N-phase voltage | Display 3+2 V
50 | A Phase and B Phase line voltage | Display 3+2 V
51 | B Phase and C Phase line voltage | Display 3+2 V
52 | C Phase and A Phase Line Voltage | Display 3+2 V
53 | Current of A-phase | Reverse signed '-', display 3+3 A
54 | Current of B-phase | Reverse signed '-', display 3+3 A
55 | Current of C-phase | Reverse signed '-', display 3+3 A
56 | Combined active power | Reverse signed '-', display 2+3 kw
57 | A phase active power | Reverse signed '-', display 2+3 kw
58 | B-phase active power | Reverse signed '-', display 2+3 kw
59 | C-phase active power | Reverse signed '-', display 2+3 kw
60 | Combined reactive power | Reverse signed '-', display 2+3 kvar
61 | A Phase reactive power | Reverse signed '-', display 2+3 kvar
62 | B phase reactive power | Reverse signed '-', display 2+3 kvar
63 | C phase reactive power | Reverse signed '-', display 2+3 kvar
64 | Combined Apparent Power | Display 2+3 kva
65 | A phase apparent power | Display 2+3 kva
66 | B phase apparent power | Display 2+3 kva
67 | C phase apparent power | Display 2+3 kva
68 | Combined frequency | 2+1Hz
69 | A phase frequency | 2+1Hz
70 | B phase frequency | 2+1Hz
71 | C phase frequency | 2+1Hz
72 | Combined power factor | Signed capacitive 'C' and inductive 'L', signed '-' (based on active power),display 1+3
73 | A phase power factor | Signed capacitive 'C' and inductive 'L', signed '-' (based on active power),display 1+3
74 | B Phase power factor | Signed capacitive 'C' and inductive 'L', signed '-' (based on active power),display 1+3
75 | C Phase power factor | Signed capacitive 'C' and inductive 'L', signed '-' (based on active power),display 1+3
Settings page
page number | Display content | Display description | Press the right button for more than 3 seconds to input the correct password
1 | Modbus ID | 1-247
2 | Baud rate | 9600/19200/38400/115200
3 | Partiy | Odd/Even/None
4 | stop bit | 1/2bit
5 | scrolling time | 5-99 seconds, 0 disables scroll display
6 | Combined code | 1=Total=Forward 2=Total=Reverse 3=Total=Forward+Reverse 4=Total=Forward-Reverse
7 | Demand Type and Period | type 0 interval 1 slip, period 1-30 minutes
8 | SO constant | 800, 1000, 1600, etc. above 100,divisible by 96000
9 | Date | DDMMYY
10 | Time | HHMMSS
11 | Reset the active resettable energy | After long press, the total (total, forward and reverse) and each phase (total, forward and reverse) can be reset, and the corresponding data can be selected to reset
12 | Reset the reactive resettable energy | After long press, the total (total, forward and reverse) and split-phase (total, forward and reverse) can be reset, and the corresponding data can be selected to reset
13 | Reset the active maximum demand | After long press, the total (total, forward and reverse) and split-phase (total, forward and reverse) can be reset, and the corresponding data can be selected to reset
14 | Reset the reactive maximum demand | After long press, the total (total, forward and reverse) and split-phase (total, forward and reverse) can be reset, and the corresponding data can be selected to reset
15 | password | 4 bits
16 | Quit | exit settings
Button | short press | long press more than 3s
Left button | Turn page | Switch the display page: Scroll display page->A-phase engergy page->B-phase engergy page->C-phase energy page->Information page->scroll page Setting page or input password page: long press to return to scroll display page
Right button | Turn page | Enter the setting page/determine the setting parameters
Other instructions: Press the button for 60 seconds without any operation, the page stays on the non-total engery & instantaneous parameter page, and automatically returns to the total engery & instantaneous parameter page